## Sheet1
GAS WATER HEATERS
TAG | MANUFACTURER | MODEL | LOCATION | ASME | WATER |  |  |  |  | FUEL |  |  |  | ELECTRICAL |  |  |  | VENTING |  | DIMENSIONS
[5 empty] | TEMP RISE (°F) | GPM | SYSTEM OUTLET TEMP (°F) | CONNECTION SIZE | MAX. PRESSURE | BTU INPUT | EFFICIENCY | TYPE | CONNECTION SIZE | V | PH | HZ | AMPS | AIR INTAKE DIA. | EXHAUST DIA. | HEIGHT | WIDTH | DEPTH | WEIGHT
| Intellihot | iN251 | Indoor | HLW | 70 | 5.6 |  | 1-1/2" NPT | 150 PSI | 251000 | 98% |  | 1-1/2" NPT | 120 | 1 | 60 | 9 | 3" | 3" | 67.5" | 20" | 20" | 266 lbs.
NOTES:
1. Tankless water heater
2. Water heater must be floor mounted.
3. Water heater is capable of wi-fi connectivity and monitoring.
4. Water heater has touch screen display.
5. Provided with manufacturer supplied strainer.
6. Provided each water heater with manufacturer supplied condensate neutralization kit, part number CN1001.
7. Water heater must have 6 year heat exchanger and 2 year parts warranty.
8. Water heater is ASME HLW stamped.
9. Water heater contains coiled stainless steel floating heat exchanger.
Contact your local INTELLIHOT representative for pricing and appliction verification: Cody Horn, chorn@intellihot.com, 937-608-3265