## Sheet1
GAS WATER HEATERS
TAG | MANUFACTURER | MODEL | LOCATION | ASME | WATER |  |  |  |  | FUEL |  |  |  | ELECTRICAL |  |  |  | VENTING |  | DIMENSIONS
[5 empty] | TEMP RISE (°F) | GPM | SYSTEM OUTLET TEMP (°F) | CONNECTION SIZE | MAX. PRESSURE | BTU INPUT | EFFICIENCY | TYPE | CONNECTION SIZE | V | PH | HZ | AMPS | AIR INTAKE DIA. | EXHAUST DIA. | HEIGHT | WIDTH | DEPTH | WEIGHT
| Intellihot | iN501 | Indoor | HLW | 70 | 13.8 |  | 1-1/2" NPT | 160 PSI | 499999 | 96% |  | 1-1/2" NPT | 120 | 1 | 60 | 9.5 | 4" | 4" | 67.5" | 20" | 20" | 345 lbs.
NOTES:
1. Tankless water heater
2. Water heater must be floor mounted.
3. Water heater must contain built-in redundancy.
4. Water heater is capable of celluar connectivity and remote monitoring.
5. Water heater has touch screen display.
6. Provided with manufacturer supplied y-strainer.
7. Provided with manufacturer supplied condensate neutralization kit.
8. Provide Honeywell Automatic Reset High Limit 210° maximum temp. to be installed on water heater outlet piping.
9. Water heater must have 10 year heat exchanger and 2 year parts warranty.
10. Water heater contains coiled stainless steel floating heat exchanger.
Contact your local INTELLIHOT representative for pricing and appliction verification: Cody Horn, chorn@intellihot.com, 937-608-3265