## Sheet1
GAS WATER HEATERS
TAG | MANUFACTURER | MODEL | LOCATION | ASME | WATER |  |  |  |  | FUEL |  |  |  | ELECTRICAL |  |  |  | VENTING |  | DIMENSIONS
[5 empty] | TEMP RISE (°F) | GPM | SYSTEM OUTLET TEMP (°F) | CONNECTION SIZE | MAX. PRESSURE | BTU INPUT | EFFICIENCY | TYPE | CONNECTION SIZE | V | PH | HZ | AMPS | AIR INTAKE DIA. | EXHAUST DIA. | HEIGHT | WIDTH | DEPTH | WEIGHT
| Intellihot | iQ1001 |  | HLW | 70 | 26.7 |  | 2" FLG | 160 PSI | 1001000 | 94% |  | 1-1/4" FLG | 120 | 1 | 60 | 20 | 6" | 6" | 67.7" | 30" | 44.3" | 800 lbs.
NOTES:
1. Tankless water heater
2. Water heater must be floor mounted.
3. Water heater must contain built-in redundancy.
4. Water heater is capable of wi-fi connectivity and monitoring.
5. Water heater has touch screen display.
6. Provided with manufacturer supplied strainer.
7. Provided with manufacturer supplied condensate neutralization kit.
8. Provide Honeywell Automatic Reset High Limit 210° maximum temp. to be installed on water heater outlet piping.
9. Water heater must have 10 year heat exchanger and 2 year parts warranty.
10. Water heater contains coiled stainless steel floating heat exchanger.
Contact your local INTELLIHOT representative for pricing and appliction verification: Cody Horn, chorn@intellihot.com, 937-608-3265